TERMS OF REFERENCE

MAINTENANCE CCTV SYSTEM AT ASEAN SECRETARIAT

(Period: January 2022-31 December 2022)

The contractor shall furnish all labor, supervision, transportation, tools, materials and supplies necessary to perform maintenance CCTV system services in accordance with the guidelines established by Local Government laws, rules and regulations. The terms, conditions, provisions, specifications, and the schedule of this proposal is listed below.

- Scope of Work

- CCTV Maintenance Services will be conducted at ASEAN Secretariat (Heritage Building and New Building), Jl. Sisingamangaraja No. 70A, Kebayoran Baru, Jakarta Selatan and Secretary-General’s Residence (SG’s Residence), Jl. Imam Bonjol, No 49, Menteng, Jakarta Pusat.

- Selected vendor shall provide services report after conducting servicing. The report shall be signed by both the serviceman and whoever in charge at the time of service includes ASEC staff.

- Asking about the problems experienced during using the CCTV system to CCTV operator staff

- Service for CCTV maintenance contracts and make visual visits of all major components (including cables and connections) such as:

1. Camera & Electricity

- Camera inspection of damage caused by dust, rain & corrosion

- View camera quality check

- Check for completeness on the camera bracket

- BNC & RCA connector inspection on Camera and DVR

- Check the camera's lens focus to work properly

- Cover Camera Check

- Check AC & DC electrical network (Adapter)

- IR Camera check (if any)

- Camera cable network check

- Clean the Housing Camera if needed

2. Control Management

- Conduct visual inspections of all components of Control Management

- Parallel monitor network / Central Area

- Check the monitor server (if any)

- Internet / server area network connection (if any)

3. Digital Video Recorder "Stand Alone"

- Inspection of DVR adapter & electrical network

- Date & Time Check (Up Date)

- Examination of recording results & movements

- Record storage capacity check (Hard disk)

- Check the internet network (if the online connection is CCTV)

- Backing Up Record Data (If there are Data Needs)

- System development Menu / Program (Up Grade Software)

- Technical Specification

Vendor should maintain the equipment as list as follow:

Monitor

1. Monitor CCTV Samsung 			3 pcs

2. Monitor Phillips				1 pcs

3. Monitor DELL 				1 pcs

4. Monitor LG					3 pcs

DVR

5. Hikvision	6 pcs (5 at Heritage Building and 1 at SG Residence)

NVR

6. NVR					3 pcs (Server Room Level 6 North)

Camera CCTV

7. Camera CCTV (with various brands) 	185 pcs (at ASEAN Secretariat Building, outdoor and indoor type) + 5 pcs (at SG Residence)

- Maintenance Schedule

Vendor should do site visit as schedule below:

- Monthly Visit of maintenance to Back up device: camera, DVR, cable for emergency

- 2 Times preventive maintenance per year to Check all device, system and installation

- On call basis for urgent matter relate to CCTV system, vendor should come to come check minimum 4 hours since receiving call from user

- Contractor Requirement and Qualification

- Contractor must have minimum 3 years’ experience in maintenance CCTV security system and technology (evidence is required)

- Contractor is highly recommended to attend preliminary site visit to check existing condition in order to ensure that the proposal submitted will cover all the possible condition

- Contractor required to prepare monthly/annual preventive maintenance schedule plan to be submit along with quotation

- Contractor is required to do all the work items by supplying the work in professional manner in accordance with the standard engineering practice and Indonesian Standard (SNI)

- Duration of Service

The successful vendor shall be committed to perform the services for the duration of one (1) year starting from January 2022 to 31 December 2022.

- Term of Payment

Payment of services will be made in monthly basis upon the signing of the Agreement and the quotation should in IDR (Rupiah)

- Validity of Quotation

Received Quotation shall be valid until 31 December 2021