## Spec Form- MCFA, Pump, FM200
For Invitations
SPECIFICATION FORM
Quotation for Maintenance Fire Fighting Systems ASEC New Building & Heritage Building
Closing date for Quotation Submission: [Procurement to fill in]
No. | Items Description |  | Qty | UoM | Unit Price (IDR) | Total Price (IDR)
General Requirements : Maintenance Fire Fighting Systems ASEC New Building & Heritage Building 1. Contractor must have minimum 5 years experiences in Fire Fighting Systems (Fire Alarms, Fire Pumps, Fire Suppression) 2. Contractor must submit Certificate/Letter from Principle of Siemens & Kidde Indonesia (For Fire Alarms & Fire Suppression) 3. Contractor must submit the work method that will be used during maintenance as one of considerations for contractor appointment 4. Conduct & provide module training session to technician in charge in operation fire alarm system, fire suppression system & fire pump system
1 | Fire Alarms ASEC New Building
| General Check, repair & troubleshooting of current alarm system at new building (north and south tower) |  | 1 | lot | [vendor to fill in] | [vendor to fill in]
| Connect interface system of Pressurization Fan Fl. 2 (North & South tower) |  | 1 | lot | [vendor to fill in] | [vendor to fill in]
2 | Fire Suppression ASEC New Building
| Inspection & maintenance of Fire Suppression Systems at Library & Data Center ASEC New Building (consist of 7 can) 1. Check, repair & troubleshooting the condition of Fire Suppression System 2. Conduct functional test of Fire Suppression systems |  | 1 | lot | [vendor to fill in] | [vendor to fill in]
| Inspection & maintenance of Fire Suppression Systems at Genset, LVMDP & MVMDP Area ASEC New Building (consist of 12 can) 1. Check, repair & troubleshooting the condition of Fire Suppression System 2. Conduct functional test of Fire Suppression systems |  | 1 | lot | [vendor to fill in] | [vendor to fill in]
3 | Fire Pump ASEC New Building & Heritage Building
| Normalization of Fire Pumps Systems (2 Fire Jockey Pumps, 2 Fire Electrical Pumps & 2 Fire Diesel Pumps) 1. Fixing leaking pipe 2. Fixing & resetting pressure switch electrical & diesel pump 3. Conduct functional test of electrical & diesel fire pump |  | 1 | lot | [vendor to fill in] | [vendor to fill in]
4 | Fire Alarms ASEC Heritage Building
| Inspection fee of Fire Alarm System and Installation point. 8 storey of heritage building (estimation 180 points) as well as Fire Alarm Master Panel (semi-addressable) |  | 1 | lot | [vendor to fill in] | [vendor to fill in]
Note: 1. The scope of work to check the heat & smoke detector device function normal but not include to replace broken device (heat & smoke detector) 2. Fixing troubleshooting in small category can be done during the inspection 3. Reporting to ASEAN Secretariat about all finding and provide recommendation
Total | [5 empty] | 0
Delivery date |  | : After PO
Availability of stock |  | : Yes
Warranty (required/optional/not required) |  | : not required
Terms of payment |  | : Downpayment 20%, 80 % After Completion
Validity of Quotation |  | : 60 days of the Quotation Date
General guideliens /Ketentuan:
1 | Please attach this Specifications Form to your quotation with your signature below or company's stamp;
Mohon melampirkan Spec. form ini pada penawaran disertai tanda tangan PIC atau stempel perusahaan;
By signing this Specification Form, you/your company agree to fulfil with all requirements as stated above.
Dengan menandatangani Form Spesifikasi ini, Anda/perusahaan Anda setuju untuk memenuhi semua kriteria tersebut diatas.
2 | Please state the availability of stocks for the above items;
Mohon cantumkan ketersediaan stock barang-barang diatas;
3 | All items provided shall be genuine. Shall the above items provided are not genuine, we will cancel the purchase of the above items;
Semua barang yang disediakan wajib barang asli. Apabila setelah pengiriman barang-barang di atas ditemukan tidak asli,
maka kami akan membatalkan Purchase Order yang sudah diterbitkan.
4 | The price in this quotation shall be valid for 30 days commencing on the date of submission of quotation;
Harga satuan yang tertera pada penawaran wajib berlaku selama 30 hari terhitung sejak tanggal penawaran;
5 | ASEAN Secretariat is exempt from the imposition of Value Added Tax. However, vendor may use Faktur Pajak 010 to collect VAT.
ASEAN Secretariat dibebaskan dari Pajak Pertambahan Nilai (PPn). Akan tetapi, vendor dapat menggunakan Faktur Pajak 010 untuk memungut PPn.
[Signature or Company's Stamp]
[Vendor to fill in]
…………………………………..
Contact Person:
Company:
Date/Tanggal: