TERMS OF REFERENCE

REPLACEMENT OF MAIN CONTROL FIRE ALARM (MCFA)

AT ASEC HERITAGE BUILDING

- BACKGROUND

The ASEAN Secretariat was established in February 1976 by the Foreign Ministers of ASEAN. It was first housed at the Department of Foreign Affairs of Indonesia in Jakarta and moved to the current location at 70A Jalan Sisingamangaraja, Jakarta since 1981.  Currently, the ASEAN Secretariat (ASEC) is housed at two buildings:

- The Heritage Building which established in 1981. The building has 9 stories with approximately 11,000 sqm in total areas.

- The New Building which was established in 2019. The building consists of two towers, and each has 16 stories with approximately 44,000 Sqm in total area. It is located adjacent to the Heritage Building.

Since its establishment, the ASEAN Secretariat Heritage Building has served as a central hub for ASEAN's operations and initiatives. The building is not only a symbol of ASEAN's unity but also an essential workspace for the Secretariat's activities. In 2014, the Main Control Fire Alarm (MCFA) system in the ASEAN Secretariat Heritage Building was upgraded to ensure safety and compliance with standards. However, despite this upgrade, the system remains based on conventional technology and during annual inspection by Fire Brigade, it was found that the MCFA was facing troubles & had become obsolete and it raising to significant safety concerns.

The proposed upgrade involves replacing the current system with a fully addressable MCFA system, which will improve reliability, accuracy, and response time during emergencies. This upgrade is necessary to maintain the building's safety and meet current fire safety standards by local authority.

The ASEAN Secretariat seeks professional vendors with the expertise to implement this critical upgrade, ensuring the continued protection of the ASEAN Secretariat Heritage Building and its occupants.

- OBJECTIVE

The objective of this work is to replace the Main Control Fire Alarm (MCFA) system at the ASEAN Secretariat Heritage Building, upgrading the existing system to a fully addressable MCFA system and connected to New Building control room.

- EXPECTED DELIVERABLES

- Completed replacement work of the existing conventional MCFA system with a fully addressable MCFA system, which has been thoroughly tested and is connected to the annunciator in the New Building control room.

- Manual books and instructions to repair or troubleshoot new MCFA System.

- SCOPE OF WORKS

The Scope of Works for the Replacement of Main Control Fire Alarm (MCFA) System at ASEC Heritage Building are as follows:

- Preparation of works by providing manpower, tools, materials, safety equipment and necessary protection to prevent damage of other building items during the working process (safety barrier).

- The contractor is responsible for carefully removing the existing MCFA system components (e.g., control panels, detectors, strobes, and other accessories) that are in the way.

- The contractor shall install the new fully addressable MCFA system, including all control panels, detectors, manual call points, alarms, and necessary wiring. The installation must consider the following:

- The Main Control Fire Alarm (MCFA) and detectors must be listed by Underwriters Laboratories (UL) and approved by Factory Mutual (FM).

- The system must be connected seamlessly with the ASEC New Building’s fire protection infrastructure and meet all required fire safety regulations.

- Each component must be securely mounted, with proper anchorage, wiring, and electrical connections, in compliance with SNI standards.

- The contractor is responsible for ensuring that all components are installed with care to avoid damage during installation. Any damage caused during the installation process must be repaired or replaced by the contractor at no extra cost to ASEC.

- System Configuration, Calibration, and Testing:

- After installation, the contractor must configure and calibrate the system to ensure it operates correctly, including adjusting sensitivity, alarm volume, response settings, and time/date synchronization for each display monitor.

- The contractor must conduct thorough testing to ensure the full functionality of the system, including all control panels, detectors, alarms, and backup power systems.

- The contractor must conduct training on the proper repair, maintenance, and troubleshooting procedures for the new MCFA system.

- The contractor must include a 1-year free maintenance & warranty period as part of the project. During this period, the contractor will provide regular checks, troubleshooting, and any necessary corrective maintenance for the MCFA system at no additional cost to ASEC.

- TECHNICAL SPECIFICATIONS

The Technical Specifications for the Replacement of Main Control Fire Alarm (MCFA) System at ASEC Heritage Building are as follows:

| No. | Description | Quantity |
| --- | --- | --- |
| 1. | Main Control Fire Alarm Panel (MCFA) – Full Addressable | 1 unit |
| 2. | Annunciator Panel (at ASEC New Building) | 1 unit |
| 3. | PC Monitoring (Core i5, RAM 8GB, HDD 1TB, Monitor 21,5”) & Printer | 1 unit |
| 4. | Detectors | 600 unit |
| 5. | Horn Strobe | 30 Unit |
| 6. | Manual Pull Station & Intercom Jack phone | 30 Unit |
| 7. | Flow Switch unit & module | 9 Unit |
| 8. | Interface system to Fire Pump, Genset, Fire Alarm New Building | 1 unit |
| 9. | Cable Power, Intercom, Detectors, Riser (Fire Rated Cable) | 1 lot |
| 10. | Cable Riser (power/installation) for Annunciator (NYRGBY) | 1 lot |

- GENERAL REQUIREMENTS

- The contractor is recommended to attend the preliminary site visit to check existing condition to ensure that the proposal submitted will cover all the possible condition. ASEC will not be responsible for covering additional costs due to differing site conditions.

- The contractor must ensure that the newly installed MCFA system (Panels, control devices, wiring, and other accessories) meets all required safety standards, local best practices (SNI), and fire safety regulations, with proper testing and calibration to prevent accidents, and safeguarding ASEC property from any potential damage during installation and testing.

- The contractor shall maintain a high standard of cleanliness and tidiness in the work area during and after installation, ensuring that all equipment, tools, and waste materials are properly managed and disposed of.

- The contractor must ensure all work is carried out with minimal disruption to ASEC’s daily operations and ensure safety protocols are strictly followed during the installation process. Proof must be attached in the submitted document.

- The contractor is responsible for ensuring that the ceiling and surrounding civil works remain in good condition during the installation process. If any part of the ceiling or civil structure is damaged during the installation, the contractor must rectify and restore it to its original condition at no additional cost. Any damage caused by the contractor must be repaired to ASEC’s satisfaction.

- The contractor must provide comprehensive documentation for ASEC’s approval and training to ASEC personnel on the operation and maintenance of the new MCFA system, ensuring that the building staff is fully equipped to manage and troubleshoot the system post-installation.

- CONTRACTOR QUALIFICATIONS

- Have at least 5 years’ experience in the installation, maintenance and upgrading of fire alarm systems, particularly in office building, commercial areas, or similar facilities. A list of relevant projects must be attached in the submitted document.

- Have at least 3 successful similar projects, proven by minimum 3 reference letter. Reference letter must be attached in the submitted document.

- Have a valid business license (SIUP/NIB) or an equivalent government document related to fire alarms and/or electronics and electrical installations. Licenses must be attached in the submitted document. Submission of additional licenses related to this works will be considered as an added advantage.

- Have an authorized certification or a similar letter from the principal manufacturer, confirming their authorization to install, maintain, and service the specified MCFA system brand. Submission of additional certifications related to this works will be considered as an added advantage.

- Have a good knowledge about the project, proven by submitting work method that complies with Engineering Standards and Safety Regulations.

- Have sufficient manpower by submitting manpower information and organizational structure to complete the project & schedule of completion for the project, schedule must comply with work schedule in ASEC premises (refer to chapter IX).

- Have a valid certification and submit at least 1 (one) personnel Health and Safety License (K3 Umum) or Electrician Technician (Teknisi K3 Listrik). Copy of valid license must be attached in the submitted document.

- TERMS OF PAYMENT

The terms of payment for this project consist of a 20% Down Payment (DP). First payment 30% upon the project reach 50% completion. Second payment 45% will be due upon completion of all project works. The remaining 5% will be settled after the project finished, including the maintenance & warranty period (12 months).

- DURATION OF SERVCES AND WORK SCHEDULE

The selected vendor shall be committed to complete the work within 7 (Seven) months and follows the working schedule in accordance with the ASEC procedures as follows:

- Monday to Friday		: 5.00 pm to 10.00 pm.

- Saturday and Sunday	: 07.30 am to 10.00 pm.

The works schedule may change as instructed by ASEC.