## Spec Form-For Invitations
For Invitations
SPECIFICATION FORM
Maintenance Fire Pumps ASEAN Secretariat (ASEC) Building
Closing date for Quotation Submission: Refer to the invitation and web advertisement (asean.org)
No. | Items Description |  | Qty | UoM | Unit Price (IDR) | Total Price (IDR)
General Qualifications for vendors : - The vendor shall provide proof of minimum 3 year experience in installation and maintenance of fire pumps - The vendor must provide proposal of detailed working method, list of tools and materials that will be used for this project
A. | Conduct maintenance (check and repair) ISUZU Diesel Fire Pump at ASEC Heritage Building, which includes, but not limited to the following works:
1 | Supply and Install Oil Filter (specification refer to existing) |  | 1 | lot |  | 0
2 | Supply and Install Diesel Fuel Filter (specifcation refer to existing) |  | 1 | lot |  | 0
3 | Supply and Install Air Filter (specification refer to existing) |  | 1 | lot |  | 0
4 | Supply and Install Diesel Engine Oil Meditran SX SAE 15W40 |  | 1 | lot |  | 0
5 | Supply and Install Water Radiator Coolant 15W40 (specification refer to existing) |  | 1 | lot |  | 0
6 | Supply and Install Fuel Filter (specification refer to existing) |  | 1 | lot |  | 0
7 | Replace battery charger Trafo 220v 1 phase 27.5 V / 5A |  | 1 | unit |  | 0
8 | Supply and Install Dry Battery 12V 80AH GS |  | 2 | unit |  | 0
9 | Conduct Top Overhaul : 1. Resetting all parameters 2. Calibration of the fuel pump, injector and nozzle 3. Replace all gasket & hose 4. Lubricant and greasing pumps, checking impeller, bearings, and gland packing 5. Conduct shaft alignment check 6. Test all controller components 7. Performance test |  | 1 | lot |  | 0
B. | Conduct maintenance (check and repair) TORISHIMA Electric Fire Pump at ASEC Heritage Building - which includes, but not limited to the following works:
1 | Conduct test trigger pressure contact & running performance test |  | 1 | lot |  | 0
2 | Check and repair as required, all electrical connections, pressure switch, safety valve, etc |  | 1 | lot |  | 0
3 | Check and apply lubricant and greasing on pumps, checking impeller, bearings, and gland packing |  | 1 | lot |  | 0
C. | Conduct maintenance (check and repair) CLARKE Diesel Fire Pump at ASEC Heritage Building, which includes, but not limited to the following works:
1 | Supply and Install Oil Filter CLARKE |  | 1 | lot |  | 0
2 | Supply and Install Diesel Fuel Filter CLARKE |  | 1 | lot |  | 0
3 | Supply and Install Air Filter CLARKE |  | 1 | lot |  | 0
4 | Supply and Install Engine Oil Diesel Meditran SX SAE 15W40 |  | 1 | lot |  | 0
5 | Supply and Install Water Coolant Radiator 15W40 (specification refer to existing) |  | 1 | lot |  | 0
6 | Supply and Install Fuel Filter CLARKE |  | 1 | lot |  | 0
7 | Supply and Install Dry Battery 12V 120AH GS |  | 2 | unit |  | 0
8 | Check and apply Lubricant and greasing on pumps, checking impeller, bearings, and gland packing |  | 1 | lot |  | 0
D. | Conduct maintenance (check and repair) IDEAL Electric Fire Pump at ASEC New Building, which includes, but not limited to the following works:
1 | Conduct test trigger pressure contact & running performance test |  | 1 | lot |  | 0
2 | Check all electrical connections, pressure switch, safety valve, etc |  | 1 | lot |  | 0
3 | Check and apply lubricant and greasing on pumps, checking impeller, bearings, and gland packing |  | 1 | lot |  | 0
Notes : 1) The vendor must provide material, supporting tools, equipment and manpower to complete the work, including the worker insurance protection 2) The vendor must comply with safety standards while working and maintain work without any accident or damage to ASEC property (provide safety net, personnel protective equipment, etc). 3) The vendor is required to ensure the working area remains tidy and clean 4) Must include commissioning test and thorough inspection. Commissioning Test must be conducted by experienced operators with valid license for electrical works. 5) The vendor must provide final report before submitting final invoices working time : weekend or national holiday : 08.00am - 10.00pm
Total | [5 empty] | 0
Delivery date |  | : After PO
Availability of stock |  | : Must be completed in 2025
Warranty (required/not required) |  | : 6 month
Terms of payment |  | : 20% Down Payment, 80% after all work has been completed
Validity of Quotation |  | : 60 days
General guideliens/Ketentuan:
1 | Please attach this Specifications Form to your quotation with your signature below or company's stamp;
Mohon melampirkan Spec. form ini pada penawaran disertai tanda tangan PIC atau stempel perusahaan;
By signing this Specification Form, you/your company agree to fulfil with all requirements as stated above.
Dengan menandatangani Form Spesifikasi ini, Anda/perusahaan Anda setuju untuk memenuhi semua kriteria tersebut diatas.
2 | Please state the availability of stocks for the above items;
Mohon cantumkan ketersediaan stock barang-barang diatas;
3 | All items provided shall be genuine. Shall the above items provided are not genuine, we will cancel the purchase of the above items;
Semua barang yang disediakan wajib barang asli. Apabila setelah pengiriman barang-barang di atas ditemukan tidak asli,
maka kami akan membatalkan Purchase Order yang sudah diterbitkan.
4 | The price in this quotation shall be valid for 60 days commencing on the date of submission of quotation;
Harga satuan yang tertera pada penawaran wajib berlaku selama 30 hari terhitung sejak tanggal penawaran;
5 | ASEAN Secretariat is exempt from the imposition of Value Added Tax. However, vendor may use Faktur Pajak 010 to collect VAT.
ASEAN Secretariat dibebaskan dari Pajak Pertambahan Nilai (PPn). Akan tetapi, vendor dapat menggunakan Faktur Pajak 010 untuk memungut PPn.
Signature and or Company Stamp
Contact Person:
Company:
Date/Tanggal: