## Fire Stop and Door
For Invitations
SPECIFICATION FORM
Fire Stop and Fire Door for Electrical and Pipe Shaft at Heritage Building
Closing date for Quotation Submission: [Procurement to fill in]
No. | Items Description |  | Qty | UoM | Unit Price (IDR) | Total Price (IDR)
General Requirements : Fire Stop and Fire Door for Electrical and Pipe Shaft at Heritage Building 1. The contractor must have a minimum of 2 years of experience in the fire and/or steel door installation and fire stop construction and/or structure casting concrete (proof must be attached in the submitted document). 2. The Contractor shall provide the fire-rating certification for the materials supplied under this scope of work (proof must be attached in the submitted document). Notes : 1) The vendor must provide material, supporting tools, equipment, manpower, and insurance to complete the work. 2) The vendor must comply with safety standards while working and maintain work without any accident or damage to ASEC property (provide safety net, personnel protective equipment, etc). 3) The vendor is required to ensure the working area remains tidy and clean. All debris and waste materials generated from the work shall be removed from the site on a daily basis to prevent the accumulation of rubbish. 4) The vendor shall verify the actual opening dimensions and site condition prior to fabrication and installation. 5) In the event of any discrepancy between the dimensions stated in this specification and the actual existing site condition, the actual existing dimensions shall prevail, subject to Owner's approval, except for the slab thickness, which shall remain as specified. 6) The vendor shall carry out a concrete hammer test to verify that the concrete strength complies with the specified requirement. working time : weekday : 5:00pm - 10.00pm, or weekend or national holiday : 08.00am - 10.00pm
1 | Fire Stop Constructions - 1
a | Fire stop construction located within the AHU room on Floor M until Floor 7 (8 floors) - Cast-in-place reinforced concrete slab, including curing - Dimension : +- 800 (W) x 1000 (L) mm - Minimum slab thickness: 150 mm - Required fire-resistance rating: minimum 2 hours - Minimum concrete compressive strength: f’c = 25 MPa, using cementitious fire-stop mortar - Reinforcement and connection details shall be designed and proposed by the Contractor for Owner’s approval - Rearrangement and tidying of existing cables using appropriate cable management accessories, including conduit, cable ties, cable clips, cable supports, and all necessary fittings, to provide a neat, secure, and maintainable installation, and install firestop sealant in between cables |  | 8 | lot | [vendor to fill in] | [vendor to fill in]
2 | Shaft Doors - 1
a | Shaft doors - 1 installation located within the AHU room on Floor M until Floor 7 (8 floors) - Removal of existing wooden door - Supply and installation of steel door complete with frame, accessories, and all necessary fittings - Door size: 800 mm (W) x 2100 mm (H) - Door leaf, frame, reinforcement, anchorage, hardware, and installation details shall be designed and proposed by the Contractor for Owner’s approval - The fire-rated steel door assembly shall have a minimum 2-hour fire-resistance rating and shall be supported by a valid fire-rating certification - Construction of an additional 2 hour fire rated masonry wall and a practical beam above the door, with dimensions of 800 mm (W) × 700 mm (H) x 150 mm (T) |  | 8 | lot | [vendor to fill in] | [vendor to fill in]
3 | Shaft Doors - 2
a | Shaft doors - 2 installation per floor on Floor M, Floor 2, Floor 4, and Floor 6 (4 floors) - Removal of existing wooden door - Supply and installation of steel door complete with frame, accessories, and all necessary fittings - Door size: 800 mm (W) x 2100 mm (H) - Door leaf, frame, reinforcement, anchorage, hardware, and installation details shall be designed and proposed by the Contractor for Owner’s approval - The fire-rated steel door assembly shall have a minimum 2-hour fire-resistance rating and shall be supported by a valid fire-rating certification - Construction of an additional 2 hour fire rated masonry wall and a practical beam above the door, with dimensions of 800 mm (W) × 700 mm (H) x 150 mm (T) |  | 4 | lot | [vendor to fill in] | [vendor to fill in]
Total | [5 empty] | 0
Delivery date |  | : After PO; works must be completed by end of November 2026
Availability of stock |  | : Ready Stock
Warranty (required) |  | : 1 year
Terms of payment |  | : 100% after all work has been completed
Validity of Quotation |  | : 90 days
General guideliens /Ketentuan:
1 | Please attach this Specifications Form to your quotation with your signature below or company's stamp;
Mohon melampirkan Spec. form ini pada penawaran disertai tanda tangan PIC atau stempel perusahaan;
By signing this Specification Form, you/your company agree to fulfil with all requirements as stated above.
Dengan menandatangani Form Spesifikasi ini, Anda/perusahaan Anda setuju untuk memenuhi semua kriteria tersebut diatas.
2 | Please state the availability of stocks for the above items;
Mohon cantumkan ketersediaan stock barang-barang diatas;
3 | All items provided shall be genuine. Shall the above items provided are not genuine, we will cancel the purchase of the above items;
Semua barang yang disediakan wajib barang asli. Apabila barang-barang di atas ditemukan tidak asli,
maka kami akan membatalkan Purchase Order yang sudah diterbitkan.
4 | The price in this quotation shall be valid for 90 (ninety) days commencing on the date of submission of quotation;
Harga satuan yang tertera pada penawaran wajib berlaku selama 90 (sembilan puluh) hari terhitung sejak tanggal penawaran;
5 | Vendor may use Faktur Pajak 040 to collect VAT by inserting this NPWP: 0224 6469 7605 3000
Vendor dapat menggunakan Faktur Pajak 040 untuk memungut PPn dengan NPWP berikut: 0224 6469 7605 3000
6 | The ASEAN Secretariat reserves the rights to take all or only selected goods/works/services.
ASEAN Secretariat berhak untuk mengambil semua atau hanya barang/pekerjaan/jasa tertentu.
[Signature or Company's Stamp]
[Vendor to fill in]
…………………………………..
Contact Person:
Company:
Date/Tanggal: