## Spec Form- MCFA, Pump, FM200
For Invitations
SPECIFICATION FORM
Quotation for Maintenance Panel & Trafo Heritage & New Building
Closing date for Quotation Submission: [Procurement to fill in]
No. | Items Description |  | Qty | UoM | Unit Price (IDR) | Total Price (IDR)
General Requirements : Maintenance Panel & Trafo Heritage & New Building 1. The contractor must have a minimum of 3 years of experience in the maintenance services or installation of electrical systems 2. The vendor shall provide valid Company & Personnel certification in electrical works or other equal certification related to installation or maintenance services (copy of certification must be submitted in quotation) Notes : 1) The vendor must provide material, supporting tools, equipment and manpower to complete the work 2) The vendor must comply with safety standards while working and maintain work without any accident or damage to ASEC property (provide safety net, personnel protective equipment, etc). 3) The vendor is required to ensure the working area remains tidy and clean 4) Must include commissioning test and thorough inspection & minor repair for all items. Commissioning Test must be conducted by experienced operators with valid license for electrical works. 5) The vendor must provide final report before submitting final invoices 6) The vendor must coordinate with PLN working time : weekend or national holiday : 08.00am - 10.00pm or 5:00pm - 5am
1 | Conduct maintenance (check and repair) Electrical Panel ASEC Heritage Building, which includes, but not limited to the following works:
| - Cleaning Panel (removal dust, cleaning busbar, relay, MCB, and other electrical components) - Functional test of MCCB/MCB, contactor, relay, pilot lamp, selector switch, and other control components - Thermographic inspection of incoming and outgoing terminals, busbar joints, MCCB/MCB terminals, cable joints, and other electrical connection points - Check abnormal temperature, overheating, hot spots, and phase temperature imbalance - Recording and documentation of thermographic results |  | 72 | Unit | [vendor to fill in] | [vendor to fill in]
Check & Repair: - MCCB/MCB rating and condition - Breaker mechanical operation - Overload relay and protection devices - Contactor and auxiliary contact operation - Control relay, timer, selector switch, push button, and indicator lamp - Verification of protection and control wiring
- Retightening jointing and termination at incoming and outgoing terminals - Retightening MCCB/MCB, busbar, contactor, terminal block, cable lug, grounding, and neutral connections - Checking loose, overheated, oxidized, or damaged terminals - Retightening using appropriate torque wrench based on manufacturer recommendation
2 | Conduct maintenance (check and repair) Electrical Panel ASEC New Building, which includes, but not limited to the following works:
| - Cleaning Panel (removal dust, cleaning busbar, relay, MCB, and other electrical components) - Functional test of MCCB/MCB, contactor, relay, pilot lamp, selector switch, and other control components - Thermographic inspection of incoming and outgoing terminals, busbar joints, MCCB/MCB terminals, cable joints, and other electrical connection points - Check abnormal temperature, overheating, hot spots, and phase temperature imbalance - Recording and documentation of thermographic results |  | 120 | Unit | [vendor to fill in] | [vendor to fill in]
Check & Repair: - MCCB/MCB rating and condition - Breaker mechanical operation - Overload relay and protection devices - Contactor and auxiliary contact operation - Control relay, timer, selector switch, push button, and indicator lamp - Verification of protection and control wiring
- Retightening jointing and termination at incoming and outgoing terminals - Retightening MCCB/MCB, busbar, contactor, terminal block, cable lug, grounding, and neutral connections - Checking loose, overheated, oxidized, or damaged terminals - Retightening using appropriate torque wrench based on manufacturer recommendation
3 | Install Acrylic Cover for Transformator 1600Kva ASEC Heritage Building
| Supply & Install Acrylic Cover for Transformator 135cm x 70 cm x 70cm |  | 1 | lot | [vendor to fill in] | [vendor to fill in]
Cleaning Trafo
Retightening Jointing / Termination at outgoing terminal
Total | [5 empty] | 0
Delivery date |  | : After PO, the work must be complete by end of december 2026
Availability of stock |  | : Yes
Warranty (required/optional/not required) |  | : 6 Months
Terms of payment |  | : Downpayment 20%, 80 % After Completion
Validity of Quotation |  | : 90 days of the Quotation Date
General guideliens/Ketentuan:
1 | Please attach this Specifications Form to your quotation with your signature below or company's stamp;
Mohon melampirkan Spec. form ini pada penawaran disertai tanda tangan PIC atau stempel perusahaan;
By signing this Specification Form, you/your company agree to fulfil with all requirements as stated above.
Dengan menandatangani Form Spesifikasi ini, Anda/perusahaan Anda setuju untuk memenuhi semua kriteria tersebut diatas.
2 | Please state the availability of stocks for the above items;
Mohon cantumkan ketersediaan stock barang-barang diatas;
3 | All items provided shall be genuine. Shall the above items provided are not genuine, we will cancel the purchase of the above items;
Semua barang yang disediakan wajib barang asli. Apabila setelah pengiriman barang-barang di atas ditemukan tidak asli,
maka kami akan membatalkan Purchase Order yang sudah diterbitkan.
4 | The price in this quotation shall be valid for 90 days commencing on the date of submission of quotation;
Harga satuan yang tertera pada penawaran wajib berlaku selama 90 hari terhitung sejak tanggal penawaran;
5 | ASEAN Secretariat is exempt from the imposition of Value Added Tax. However, vendor may use Faktur Pajak 010 to collect VAT.
ASEAN Secretariat dibebaskan dari Pajak Pertambahan Nilai (PPn). Akan tetapi, vendor dapat menggunakan Faktur Pajak 010 untuk memungut PPn.
6 | The ASEAN Secretariat reserves the rights to take all or only selected goods/works/services.
ASEAN Secretariat berhak untuk mengambil semua atau hanya barang/pekerjaan/jasa tertentu.
Signature and or Company Stamp
Contact Person:
Company:
Date/Tanggal: